Attachment 1: Example Preventive Maintenance Schedule

It is highly recommended that schools have a preventive maintenance schedule--edit according to operational needs of each school building. Consult HVAC contractor, HVAC vendors, flooring manufacturer, cleaning product vendor, facility staff, etc.

|  | Daily | Weekly | 3 Months | 6 Months | Yearly | 2 Years | As Needed |
| --- | --- | --- | --- | --- | --- | --- | --- |
| AIR HANDLING UNITS |  |  |  |  |  |  |  |
| Intake unobstructed |  |  | x |  |  |  |  |
| Air Flows In |  |  | x |  |  |  |  |
| No Pollutant Sources Nearby |  |  | x |  |  |  |  |
| Intake Dampers Operational |  |  | x |  |  |  |  |
| Outdoor Damper Open (at least 10%) |  |  | x |  |  |  |  |
| Filters Replaced/Fitted Properly |  |  | x |  |  |  |  |
| Moisture (e.g., drain pans) |  |  | x |  |  |  |  |
| Cleanliness |  |  | x |  |  |  |  |
| Belts |  |  |  |  | x |  |  |
| Lubrication |  |  |  |  | x |  |  |
| Cleaning of Heating & Cooling Coils |  |  |  |  | x |  |  |
| Cleaning of Drainage Areas |  |  |  |  | x |  |  |
| Calibration of Sensors & Controls |  |  |  |  |  | x |  |
| Cleaning of Ductwork |  |  |  |  |  |  | x |
| Airflow Balancing |  |  |  |  |  |  | x |
| Remove Snow Around Intakes, Exhaust, Stacks |  |  |  |  |  |  | x |
| LOCAL EXHAUST SYSTEMS |  |  |  |  |  |  |  |
| Functional |  |  |  |  | x |  |  |
| Correct Air Direction |  |  |  |  | x |  |  |
| Rooftop Fans Undamaged & Unobstructed |  |  |  |  | x |  |  |
| Proper Exhaust Air Volume |  |  |  |  |  | x |  |
| GENERAL BUILDING CLEANING |  |  |  |  |  |  |  |
| Garbage | x |  |  |  |  |  |  |
| Carpet and Hard Floors | x |  |  |  |  |  |  |
| Wet Mop Hard Floors |  | x |  |  |  |  |  |
| Tables |  | x |  |  |  |  |  |
| Entry Mats |  | x |  |  |  |  |  |
| Cushions & Upholstered Furniture |  |  | x |  |  |  |  |
| Shelves, & Cupboard Tops |  |  | x |  |  |  |  |
| Ventilation Diffusers |  |  | x |  |  |  |  |
| Provide each Room with All-purpose Green cleaner |  |  | x |  |  |  |  |
| Check & Maintenance Vacuum Cleaners |  |  | x |  |  |  |  |
| Deep Clean Carpets & Re-finish Hard Floors |  |  |  | x |  |  |  |
| Spot Deep Clean Small Spills/Stains |  |  |  |  |  |  | x |
| OTHER |  |  |  |  |  |  |  |
| Fill/Flush: floor drains, unused sinks & toilets |  | x |  |  |  |  |  |
| Thermostats Functional |  |  | x |  |  |  |  |
| Moisture Inspection: ceiling, plumbing, roof, exterior |  |  | x |  |  |  |  |
| Check Hazardous Chemicals Storage |  |  |  |  | x |  |  |
| Replace Stained Ceiling Tiles |  |  |  |  | x |  | x |

Your preventive maintenance schedule could include examining:

- Light fixtures for burnt-out lamp ballasts

- Proper shielding of outdoor air intakes to prevent entry of wind driven rain and snow

- Measuring fresh air supply rates and comparing to design specifications, to see whether the HVAC system is delivering adequate fresh air for the space and number of people it serves

- Fresh air supply intake more frequently, to see if it’s cut off

- Unit ventilators more frequently than other ventilation equipment to see if cleaning should be done more often (such as every month)

- Plumbing hardware for inappropriate sizing

- Landscaping and grounds operations (such as presence of mud at building entrances, sloping land away from buildings, pest entry points, grass clippings discharged into unit vents)

- Attic insulation and ventilation to keep the attic tempered, and reduce the problem of ice dams on the roof

- Different areas seasonally (create a different checklist for each season)