### VSPC Project Priority List
A list of electric reliability deficiencies, when they are projected to occur and the timing of efforts to address them

##### Background

The Vermont System Planning Committee (VSPC) is required to adopt, and file with the Public Service Board, a prioritized list of identified electric system reliability deficiencies. This prioritized list must contain a schedule of dates for analyzing the deficiencies and determining solutions. Once the list is in place, utilities must adhere to its schedule or inform the Board of any deadlines they cannot meet.

The Memorandum of Understanding establishing the VSPC details the elements that must be included in the project priority list for each reliability deficiency, including:

- The reason for the priority assigned to each reliability deficiency.

- If the likely transmission solution has not yet been identified, the date by which the analysis of the transmission solution is proposed to be completed.

- The date by which analysis of non-transmission alternatives (NTAs) is proposed to be completed.

- The date by which a decision will be made concerning solution selection, implementation strategy, and cost allocation.

This document comprises the project priority list of the VSPC. The list serves multiple purposes: laying out the work of the VSPC for the next several years; providing the public with a tool, in addition to the VSPC annual report and the VELCO Long-Range Transmission Plan, for understanding where reliability deficiencies are projected to occur prior to the planning of specific transmission projects or non-transmission alternatives; and keeping regulators apprised of the work that is anticipated and its schedule.

##### Organization of the list

The list is organized in priority order from highest priority, i.e., most immediate projected need, to lowest priority, i.e., longest-range projected need. Some reliability deficiencies are grouped together in the same priority because they may be addressed by a common transmission solution.

According to the terms of the Memorandum of Understanding in Docket 7081 (MOU), the priority list is meant to address reliability deficiencies that were identified in the 2006 VELCO Long-Range Transmission Plan (LRTP).  Although, the Gorge Area Reinforcement project and the Tafts Corner Phase II project were not explicitly mentioned in the 2006 Plan, they are included in the Essex transformer Reliability Deficiency because they help mitigate this deficiency. Therefore, these two projects are incorporated into the list with the same priority level as other projects related to the Essex Reliability Deficiency.

As noted in the MOU, VELCO will be responsible for performing transmission and NTA analyses for bulk and primarily bulk system deficiencies. For subsystem or primarily subsystem deficiencies, the Affected Utilities are responsible for performing these studies.

All acronyms appear in a glossary at the back of the report.

##### Summary of the list

The following map shows the rough location of the priorities included in the list followed by a summary list of the projects included in each.

Priority 1
Coolidge Connector; Bennington and Brattleboro transformers; Vermont Yankee transformers; Vermont Yankee to Coolidge line; Bennington transformer

Priority 2
East Avenue Loop; Gorge Area Reinforcement; upgrade of Essex transformers.

Priority 3
St. Johnsbury transformer

[For illustration of the level of detail for this summary.]

THIS PAGE IS A PLACEHOLDER FOR THE ACTUAL MAP

##### A note about how reliability deficiencies are identified

The adequacy of the electrical system is assessed by testing equipment outages, also known as contingencies, under various system conditions, such as load level, generation dispatch and power transfer levels.  A reliability deficiency occurs when performance criteria are violated.  Examples of performance criteria are that electrical facilities shall remain below their normal capacity prior to a contingency, and below their emergency capacity following a contingency.

##### Detailed Priority List

Priority 1: Southern Loop

Priority 1 includes the four deficiencies that will be addressed by the Coolidge Connector project, for which VELCO and Central Vermont Public Service applied for a Certificate of Public Good (CPG) from the Public Service Board in November 2007. The review process is underway in Docket 7373. The deficiencies to be addressed include:

- Loss of 115/46 kV transformers into Bennington or Brattleboro area would cause loss of significant load in Southern Vermont.

- Loss of the Vermont Yankee 345/115 kV autotransformer would place Brattleboro area load at high risk until a replacement transformer can be installed.

- Loss of the Vermont Yankee to Coolidge 345 kV line would cause significant voltage/thermal concerns.

- Loss of one Bennington 115/46 kV transformer would overload the other.

Reason for priority:

The priority level of these projects is based on the fact that a transmission solution to address the deficiencies is presently under consideration by the Public Service Board (PSB) for a CPG.  In addition, these deficiencies affect a very large area of the state.

| Completion date of Transmission analysis: | The transmission analysis was completed prior to the filing of the application for a Certificate of Public Good. |
| --- | --- |
| Completion date of NTA SCREENING/analysis: | The NTA analysis is completed. |
| Expected date of a decision concerning solution selection, implementation strategy, and cost allocation: | Decisions for solution selection, implementation strategy, and cost allocation were made. |

Priority 2: Loss of Essex transformer

Priority 2 includes one reliability deficiency that was considered in the Burlington Waterfront Area-Specific Collaborative (ASC) and the Digital Injection ASC. The relevant reliability deficiency is:

- Loss of one Essex 115/34.5 kV transformer may overload the other (at a time when the McNeil generation plant is unavailable), with consequent load shedding in the [describe geographical area].

The transmission solutions developed by the ASCs would each reduce load on the Essex transformers by either adding another source to the 34.5 kV network or by removing load from the 34.5 kV network to the Tafts Corner 115/12.5 kV radial transformers. The Burlington Waterfront ASC involves three phases:

- Phase 1: The East Avenue Loop. This project has received a Certificate of Public Good.

- Phase 2: The Gorge Area Reinforcement. This project is expected to be submitted to the Public Service Board to obtain a Certificate of Public Good by July 2008.

- Phase 3: Upgrade of the Essex transformers.

The Digital Injection ASC also involves three phases:

- Phase 1: Tafts Corner 115 kV substation construction.

- Phase 2: Addition of a first Tafts Corner 115/12.5 kV transformer. This project is expected to be submitted to the Public Service Board to obtain a Certificate of Public Good in July 2008.

- Phase 3: Addition of a second Tafts Corner 115/12.5 kV transformer.

These two projects were split into multiple phases because there is a significant amount of time — five years or more — between the expected need dates of the first and last set of upgrades.  This approach allows time for non-transmission alternatives to postpone the latter phases.

Reason for priority:

The priority level of these projects is based on the fact that transmission solutions for the initial phases are either in permitting or about to be in permitting. In addition, a large amount of load is at risk in the greater Burlington area served by the Burlington Electric Department, Green Mountain Power and Vermont Electric Cooperative.

Phase 3 of both the Waterfront and Digital Injection ASC projects will be studied further, and will move forward as appropriate, based on the triggers related to load level identified in the area-specific collaborative.  The need date for these projects will depend on the growth rate of the load, the effects of geo-targeted demand side management, and the addition of reliable generation.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

|  | Waterfront | Digital Injection |
| --- | --- | --- |
| A: Transmission analysis Phase 1 Phase 2 Phase 3 | Completed Completed Completed, but to be revisited by 6/30/12 in light of possible additional generation and geo-targeting | Completed Completed June 30, 2012 |
| B: NTA screening/analysis Phase 1 Phase 2 Phase 3 | Completed May 31, 2008 December 31, 2012 | Completed May 31, 2008 December 31, 2012 |
| C: Solution selection etc. Phase 1 Phase 2 Phase 3 | Completed June 15, 2008 March 31, 2013 | Completed June 15, 2008 March 31, 2013 |

Priority 3: Loss of St. Johnsbury transformer; Voltage collapse/low voltage in northern VT due to loss of transmission at either end

The following deficiencies will be addressed by the Lyndonville/St Johnsbury project that is expected to be filed within a year.

- Loss of St. Johnsbury 115/34.5 kV transformer results in loss of all load at St. Johnsbury

- Low voltage or voltage collapse in northern Vermont for loss of transmission at either end

Reason for priority:

These deficiencies are given a priority of 3 because the selected project will be filed with the Board for section 248 approval in the next few months.  In addition, there is a large exposure to the first deficiency due to local system topology and insufficient voltage support.  This is primarily a subsystem concern.

Completion date of Transmission analysis:

The transmission analysis will be completed by May 31, 2008.

Completion date of NTA SCREENING/ANALYSIS:

The NTA analysis will be completed by October 31, 2008.

Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

The decision for solution selection will be made by November 30, 2008.  Decisions for implementation strategy, and cost allocation will be made by March 31, 2009.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | May 31, 2008 |  |
| --- | --- | --- |
| B: NTA screening/analysis | October 31, 2008 |  |
| C: Solution selection etc. -- Solution selection -- Implementation & cost allocation | November 30, 2008 March 31, 2009 |  |

Priority 4: New Haven transformer; Middlebury transformer

The following deficiencies will be addressed by the Middlebury project that will be filed within a year.

- Loss of the New Haven 115/46 kV transformer would result in unacceptable low voltages (loss of all load following completion of NRP).

- Loss of Middlebury 115/46 kV transformer would result in unacceptable low voltages locally.

Reason for priority:

These deficiencies are given a priority of 4 because of the large exposure to these deficiencies.  In addition, the selected project will be filed with the Board for section 248 approval in the next few months.  This is primarily a subsystem concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | May 31, 2008 |  |
| --- | --- | --- |
| B: NTA screening/analysis | October 31, 2008 |  |
| C: Solution selection etc. -- Solution selection -- Implementation & cost allocation | November 30, 2008 March 31, 2009 |  |

Priority 5: St. Albans transformer; East Fairfax transformer; Georgia breaker failure.

The following deficiencies will be addressed by the St Albans/Georgia project:

- Loss of one St. Albans 115/34.5 kV transformer overloads the other.

- Loss of the St. Albans transformers with loss of the 115 kV line or the East Fairfax transformer causes local voltage collapse.

- Breaker failure at Georgia substation results in unacceptable voltage / thermal performance locally.

Reason for priority

These deficiencies are given a priority of 5 because they could occur at load levels as low as 850 MW.  This is primarily a subsystem concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | July 1, 2009 |  |
| --- | --- | --- |
| B: NTA screening/analysis | July 1, 2010 |  |
| C: Solution selection etc. | December 31, 2010 |  |

Priority 6: North Rutland/Cold River

Loss of either the North Rutland or Cold River 115/46 kV transformer would overload the other unit with unacceptable low voltages locally.

Reason for priority

This deficiency is given a priority of 6 because it could occur at load levels as low as 930 MW, and because of the amount of load affected.  This is primarily a subsystem concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | December 31, 2008 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 7: West Rutland, Blissville

Loss of West Rutland - Blissville 115 kV line causes unacceptable low voltages locally

Reason for priority

This deficiency is given a priority of 7 because it could occur at load levels as low as 920 MW.  This is primarily a subsystem concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | December 31, 2008 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 8: Hartford transformer

Loss of the Hartford 115/46 kV transformer would cause unacceptable low voltages locally.

Reason for priority

This deficiency is given a priority of 8 because it could occur at load levels as low as 950 MW.  This is primarily a subsystem concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | December 31, 2008 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 9: Loss of PV20 underground causeway cable from Apple Tree to pole 172

Long term loss of PV20 underground causeway cable with many other outages can cause severe & widespread voltage / thermal concerns.

Reason for priority

This deficiency is given a priority of 9 because it could occur at load levels as low as 1100 MW, and a significant amount of load could be affected.  This is a bulk system concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | May 31, 2009 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 10: Ascutney breaker failure

Breaker failure at Ascutney substation results in unacceptable voltage / thermal performance locally

Reason for priority:

This deficiency is given a priority of 10 because it could occur at the 1200 MW load level.  This is primarily a subsystem concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | May 31, 2009 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 11: Coolidge transformer

Long term loss of Coolidge 345/115 kV transformer causes voltage and thermal concerns in Central Vermont.

Reason for priority:

This deficiency is given a priority of 11 because it could occur at the 1250 MW load level.  This is primarily a bulk system concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | May 31, 2009 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 12: Barre to Berlin; Florence to West Rutland; Cold River to North Rutland

The following deficiencies occur at the same load level, and are similar.

- Overload of the Barre to Berlin 115 kV line

- Overload of the Florence to West Rutland 115 kV line

- Overload of the Cold River to North Rutland 115 kV line

Reason for priority:

These deficiencies are given a priority of 12 because they could occur at the 1300 MW load level.  This is primarily a bulk system concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | May 31, 2009 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 13: New Haven to Williston

The New Haven to Williston 115 kV line could overload when the parallel 115 kV line trips.

Reason for priority

This deficiency is given a priority of 13 because it could occur just beyond the 1300 MW load level.  This is a bulk system concern.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | May 31, 2009 |  |
| --- | --- | --- |
| B: NTA screening/analysis | December 31, 2009 |  |
| C: Solution selection etc. | March 31, 2010 |  |

Priority 14: Williston to Tafts Corners; Barre to Berlin; Berlin to Middlesex

The following deficiencies occur at the same load level, and are similar.

- Loss of the Williston to Tafts Corners 115 kV line, with heavy flows from south to north, overloads the Queen City 115/34.5 kV transformer

- Loss of the Barre to Berlin 115 kV line section, when heavily loaded from east to west, overloads the Barre transformer

- Loss of the Berlin to Middlesex 115 kV line section, when heavily loaded from east to west, overloads the Berlin transformer

Reason for priority

These deficiencies were given a priority of 14 because GMP has proposed to address them by opening the 34.5 kV at appropriate locations.  The deficiencies will need to be re-evaluated periodically to determine whether the proposed operating actions will continue to be acceptable.  This is primarily a subsystem concern.  However, sectionalizing of sub-transmission lines may result in a transmission overload sometime in the future.

A:	Completion date of Transmission analysis:

B:	Completion date of NTA Screening/analysis:

C:	Expected date of a decision concerning solution selection, implementation strategy, and cost allocation:

| A: Transmission analysis | No analysis will be performed |  |
| --- | --- | --- |
| B: NTA screening/analysis | No analysis will be performed |  |
| C: Solution selection etc. | No decisions are needed |  |

## Glossary of terms and acronyms

[in progress]

## Table of Priorities and Reliability Deficiencies

[Insert original table format as distributed in previous meetings.]

# Footnotes

The complete text of paragraph 51 is as follows: Following the filing of a Plan under 30 V.S.A. § 218c(d), and given a proposal from the Affected Utilities, the VSPC will create a priority list concerning Reliability Deficiencies identified in the Plan, which list shall be promptly filed with the Board for its information along with any comments from VSPC participants. For each Reliability Deficiency included on the list, the filing shall at a minimum state: (a) the reason for the priority assigned to the deficiency; (b) if no likely Transmission solution has yet been identified, the date by which further analysis of Transmission solutions to the deficiency is proposed to be completed; (c) the date by which NTA analysis is proposed to be completed; and (d) the date by which a decision will be made concerning solution selection, implementation strategy, and cost allocation. Upon filing by the VSPC, the NTA Analysis and decisions on solution selection, implementation strategy, and cost allocation for the subject Reliability Deficiencies shall be made in accordance with the dates contained on the filed priority list unless the Board directs otherwise. Subsequent to such filing, the Affected Utility or Utilities may make another informational filing to the Board to extend a deadline contained therein, stating the new deadline and the reason for the extension. The Department, all other participants in the VSPC, and all Parties shall be provided notice and a copy of the filing at the time priority lists or extensions thereof are submitted under this paragraph. At any time, any participant in the VSPC or Party may request Board review of whether such a priority list or extension should be modified, and the Board may initiate such review on its own motion.

Memorandum of understanding in Docket 7081, Vermont Public Service Board, approved on 6/20/07. http://www.state.vt.us/psb/orders/2007/files/7081mouwithattachments.pdf